## Summary
Heat Network Sizing Tool for 480 Properties
Dwelling Peak DHW | 65 | Kw |  | Peak DHW Load | 1000.6874 | kW | 4.7652 | l/s | Cost of Pipework | 165020.2667
Dwelling Peak CH | 3 | Kw |  | Peak CH Load | 1080 | kW | 10.2857 | l/s
DP across load (HIU+meter) | 65 | kPa |  | Peak Load | 2028.9374 | kW | 14.558 | l/s
Peak Load Flow Temperature | 80 | C
Summer Flow Temperature | 65 | C |  | Peak Load Heat Loss | 123.8097 | kW | 6.102%
Return DHW | 30 | C
Return CH | 55 | C |  | Peak Pressure Drop | 124.2494 | kPa
Occupants per property | 3 |  |  | Summer Peak Pressure Drop | 95.7777 | kPa
Flush Rate (HIU function) | 20 | l/m
Peak continuous velocity | 1 | m/s |  | Peak Pressure Drop, Building | 77.2297 | kPa
Fixed DHW/property/day | 50 | litres | info | Summer Peak Pressure Drop, Building | 82.082 | kPa
DHW/person/day | 25 | litres
DHW Temp Rise (for above) | 40 | C |  | Peak Erosion Velocity | 0.66264 | m/s | 1 | m/s max.
Hours Central Heating per Year | 500 | hours |  | Minimum Velocity | 0.37083 | m/s | 0.5 | m/s min.
Insulation Thickness | 20 | mm
Thermal Integration Ltd.
0845 2411441
www.heatweb.com
Note on C8: Peak output temperature from plantroom at -10C external weather conditions, location adjusted.
Note on C10: Based on mains at 15C

## Pipe Sizing
| Example for index flat on 480 property scheme, with 10 risers, feeding 4 storey buildings | [39 empty] | Columns W,X,Y for Herz Williams Pressure Loss Calculation
[7 empty] | Physical |  |  |  |  | Loading | [21 empty] | Pipe Selection |  |  |  | Pressure Loss | [8 empty] | Volume |  | Velocity |  |  |  |  | Thermal Losses | [8 empty] | Summer Figures
ID | Description | Class | Peak | Properties | Occupants | Daily | Length | Elbow | Elbow | Tee | Tee | Count | Total | Danish | DHW | DHW | Min | Est | Htg | Htg | DHW | Htg | DHW | Peak % | Htg | Htg | Htg % | Htg % | Total | Total | Primary | Pipe Area | Pipe Bore | Pipe Bore | Pipe Size | Material | Roughness | f = friction (mm H20 per 100 m pipe) | f = friction (kPa per 100 m pipe) | Head loss (mm H20) | kPa | Pa/m | Equiv | kPa | kPa | kPa | Area | Volume | Peak | Continuous | Weighed | Flush | Accumulative | Thermal | Peak | Peak | Standby | % Time | Standby | Standby | Average | % Share | DHW | f = friction (mm H20 per 100 m pipe) | f = friction (kPa per 100 m pipe) | Head loss (mm H20) | kPa | Pa/m | kPa | kPa | Peak | Continuous | Weighed | Tube | Tube
|  |  | Target |  |  | DHW | m | 90° | 45° | Line | Branch |  | Length | DHW | Diversity | kW | HIUs | Taps | Diversity | kw | Priority | kw | litre/s | time at | litre/s | litre/s | of Peak | of Daily | Peak | Peak | Return | mm2 | Calculated | Selected | [6 empty] | pipes |  | Length | fittings | TOTAL | Share |  | litres | Velocity | Velocity | Erosion | time | Flush time | Loss | Losses | Losses | Temp | Standby | Losses | Losses | Losses | Losses | litres/s |  |  |  | pipes |  | fittings | TOTAL | Velocity | Velocity | Erosion | Cost | Cost
|  |  | Velocity |  |  | kWh | [7 empty] | DS439 |  |  | Running | Running |  |  | Saving | NET |  | Peak | peak | minus | Flow | kWh | kW | litre/s | Temp |  |  | mm | mm | [7 empty] | fittings | [5 empty] | m/s | m/s | Velocity | seconds | seconds | W/m/K | kW | kW | C |  | kW | kW | kW |  | Summer | [7 empty] | m/s | m/s | Velocity | £/m | £
|  |  | m/s | [10 empty] | kW | [6 empty] | kW |  |  |  |  | priority |  |  |  |  | C | [19 empty] | m/s |  |  |  |  | TOTAL |  |  |  | TOTAL | TOTAL | [11 empty] | m/s
4982.512
1F | Run to 1st riser | Flow | 1 | 480 | 1440 | 2800 | 100 | 4 |  | 1 |  | 1 | 100 | 1000.6874 | 0.032073 | 1000.6874 | 23 | 83.3906 | 0.75 | 1080 | 51.75 | 1028.25 | 4.7652 | 11.66% | 10.2857 | 9.7929 | 67.27% | 89.81% | 2028.9374 | 14.558 | 46.8169 | 14558.0351 | 136.1465 | 147 | 150 | Steel | 140 | 518.4551 | 5.086 | 518.4551 | 5.086 | 50.8604 | 20.58 | 1.0467 | 6.1328 | 4.936% | 16971.6546 | 1697.1655 | 0.85779 | 0.60605 | 0.64052 | 5091.4964 | 14947.5359 | 0.90371 | 4.9704 | 4.9704 | 80 | 50% | 4.9704 | 4.9704 | 4.9704 | 2.781% | 6.8074 | 126.8603 | 1.2445 | 126.8603 | 1.2445 | 12.445 | 0.25612 | 1.5006 | 0.28077 | 0 | 0.095869 | 50 | 5000
2F | Run to 2nd Riser | Flow | 1 | 432 | 1296 | 2520 | 30 |  | 2 | 1 |  | 1 | 30 | 922.4307 | 0.03285 | 922.4307 | 21 | 76.8692 | 0.8 | 1036.8 | 50.4 | 986.4 | 4.3925 | 11.38% | 9.8743 | 9.3943 | 68.14% | 90.38% | 1908.8307 | 13.7868 | 47.0349 | 13786.8127 | 132.4912 | 147 | 150 | Steel | 140 | 468.7399 | 4.5983 | 140.622 | 1.3795 | 45.9834 | 7.644 | 0.3515 | 1.731 | 1.393% | 16971.6546 | 509.1496 | 0.81234 | 0.58181 | 0.61244 | 1527.4489 | 9856.0396 | 0.90371 | 1.4911 | 1.4911 | 80 | 0% | 1.4911 | 1.4911 | 1.4911 | 0.8344% | 6.275 | 109.1014 | 1.0703 | 32.7304 | 0.32109 | 10.7028 | 0.081813 | 0.4029 | 0.25882 | 0 | 0.087321 | 50 | 1500
3F | Run to 3rd Riser | Flow | 1 | 384 | 1152 | 2240 | 30 |  | 2 | 1 |  | 1 | 30 | 842.9633 | 0.033773 | 842.9633 | 19 | 70.2469 | 0.8 | 921.6 | 45.6 | 876 | 4.0141 | 11.07% | 8.7771 | 8.3429 | 67.52% | 90.37% | 1718.9633 | 12.357 | 46.8789 | 12356.9679 | 125.4328 | 147 | 150 | Steel | 140 | 382.7064 | 3.7543 | 114.8119 | 1.1263 | 37.5435 | 7.644 | 0.28698 | 1.4133 | 1.137% | 16971.6546 | 509.1496 | 0.72809 | 0.51716 | 0.54456 | 1527.4489 | 8328.5906 | 0.90371 | 1.4911 | 1.4911 | 80 | 0% | 1.4911 | 1.4911 | 1.4911 | 0.8344% | 5.7344 | 92.3359 | 0.90582 | 27.7008 | 0.27174 | 9.0582 | 0.069241 | 0.34099 | 0.23652 | 0 | 0.078701 | 50 | 1500
4F | Run to 4th Riser | Flow | 1 | 336 | 1008 | 1960 | 30 |  | 2 | 1 |  | 1 | 30 | 762.0497 | 0.034892 | 762.0497 | 17 | 63.5041 | 0.8 | 806.4 | 40.8 | 765.6 | 3.6288 | 10.72% | 7.68 | 7.2914 | 66.77% | 90.36% | 1527.6497 | 10.9202 | 46.6925 | 10920.2366 | 117.9156 | 147 | 150 | Steel | 140 | 304.4042 | 2.9862 | 91.3212 | 0.89586 | 29.862 | 7.644 | 0.22827 | 1.1241 | 0.9047% | 16971.6546 | 509.1496 | 0.64344 | 0.45252 | 0.47665 | 1527.4489 | 6801.1417 | 0.90371 | 1.4911 | 1.4911 | 80 | 0% | 1.4911 | 1.4911 | 1.4911 | 0.8344% | 5.184 | 76.596 | 0.75141 | 22.9788 | 0.22542 | 7.5141 | 0.057438 | 0.28286 | 0.21382 | 0 | 0.069996 | 50 | 1500
5F | Run to 5th Riser | Flow | 1 | 288 | 864 | 1680 | 30 |  | 2 | 1 |  | 1 | 30 | 679.3666 | 0.036291 | 679.3666 | 16 | 56.6139 | 0.85 | 734.4 | 40.8 | 693.6 | 3.2351 | 10.3% | 6.9943 | 6.6057 | 67.13% | 90.83% | 1372.9666 | 9.8408 | 46.7815 | 9840.7932 | 111.9361 | 147 | 150 | Steel | 140 | 251.0363 | 2.4627 | 75.3109 | 0.7388 | 24.6267 | 7.644 | 0.18825 | 0.92705 | 0.7461% | 16971.6546 | 509.1496 | 0.57984 | 0.41212 | 0.43241 | 1527.4489 | 5273.6928 | 0.90371 | 1.4911 | 1.4911 | 80 | 0% | 1.4911 | 1.4911 | 1.4911 | 0.8344% | 4.6215 | 61.9199 | 0.60743 | 18.576 | 0.18223 | 6.0743 | 0.046432 | 0.22866 | 0.19062 | 0 | 0.061187 | 50 | 1500
6F | Run to 6th Riser | Flow | 1 | 240 | 720 | 1400 | 30 |  | 2 | 1 |  | 1 | 30 | 594.4483 | 0.038106 | 594.4483 | 14 | 49.5374 | 0.85 | 612 | 35.7 | 576.3 | 2.8307 | 9.813% | 5.8286 | 5.4886 | 65.97% | 90.81% | 1170.7483 | 8.3193 | 46.4935 | 8319.2778 | 102.9196 | 147 | 150 | Steel | 140 | 183.9261 | 1.8043 | 55.1778 | 0.54129 | 18.0432 | 7.644 | 0.13792 | 0.67922 | 0.5467% | 16971.6546 | 509.1496 | 0.49019 | 0.34343 | 0.36048 | 1527.4489 | 3746.2439 | 0.90371 | 1.4911 | 1.4911 | 80 | 0% | 1.4911 | 1.4911 | 1.4911 | 0.8344% | 4.0439 | 48.354 | 0.47435 | 14.5062 | 0.14231 | 4.7435 | 0.03626 | 0.17857 | 0.16679 | 0 | 0.052248 | 50 | 1500
7F | Run to 7th Riser | Flow | 1 | 192 | 576 | 1120 | 30 |  | 2 | 1 |  | 1 | 30 | 506.5804 | 0.040591 | 506.5804 | 12 | 42.215 | 0.85 | 489.6 | 30.6 | 459 | 2.4123 | 9.212% | 4.6629 | 4.3714 | 64.44% | 90.77% | 965.5804 | 6.7837 | 46.11 | 6783.7164 | 92.9371 | 97 | 100 | Steel | 140 | 952.7251 | 9.3462 | 285.8175 | 2.8039 | 93.4623 | 5.044 | 0.47142 | 3.2753 | 2.636% | 7389.8051 | 221.6942 | 0.91798 | 0.63099 | 0.66264 | 665.0825 | 2218.795 | 0.6349 | 1.0476 | 1.0476 | 80 | 0% | 1.0476 | 1.0476 | 1.0476 | 0.5862% | 3.4461 | 271.7857 | 2.6662 | 81.5357 | 0.79987 | 26.6622 | 0.13448 | 0.93435 | 0.32643 | 0 | 0.099078 | 33.3333 | 1000
8F | Run to 8th Riser | Flow | 1 | 144 | 432 | 840 | 30 |  | 2 | 1 |  | 1 | 30 | 414.56 | 0.044291 | 414.56 | 10 | 34.5467 | 0.9 | 388.8 | 27 | 361.8 | 1.9741 | 8.443% | 3.7029 | 3.4457 | 63.58% | 91.18% | 776.36 | 5.4198 | 45.8941 | 5419.8095 | 83.0706 | 97 | 100 | Steel | 140 | 628.6774 | 6.1673 | 188.6032 | 1.8502 | 61.6733 | 5.044 | 0.31108 | 2.1613 | 1.739% | 7389.8051 | 221.6942 | 0.73342 | 0.50108 | 0.52468 | 665.0825 | 1553.7125 | 0.6349 | 1.0476 | 1.0476 | 80 | 0% | 1.0476 | 1.0476 | 1.0476 | 0.5862% | 2.8201 | 187.495 | 1.8393 | 56.2485 | 0.5518 | 18.3933 | 0.092776 | 0.64457 | 0.26714 | 0 | 0.07762 | 33.3333 | 1000
9F | Run to 9th Riser | Flow | 1 | 96 | 288 | 560 | 30 |  | 2 | 1 |  | 1 | 30 | 316.0416 | 0.050648 | 316.0416 | 8 | 26.3368 | 0.9 | 259.2 | 21.6 | 237.6 | 1.505 | 7.383% | 2.4686 | 2.2629 | 60.06% | 91.06% | 553.6416 | 3.7678 | 45.0144 | 3767.8173 | 69.2628 | 72 | 75 | Steel | 140 | 1367.0816 | 13.4111 | 410.1245 | 4.0233 | 134.1107 | 3.744 | 0.50211 | 4.5254 | 3.642% | 4071.5006 | 122.145 | 0.92541 | 0.60631 | 0.63537 | 366.4351 | 888.6301 | 0.49978 | 0.82463 | 0.82463 | 80 | 0% | 0.82463 | 0.82463 | 0.82463 | 0.4614% | 2.1499 | 483.6495 | 4.7446 | 145.0949 | 1.4234 | 47.446 | 0.17764 | 1.601 | 0.36963 | 0 | 0.10044 | 25 | 750
10F | Run to 10th riser (ground floor) | Flow | 1 | 48 | 144 | 280 | 30 | 1 | 2 |  |  | 1 | 30 | 204.9702 | 0.065696 | 204.9702 | 5 | 17.0809 | 0.9 | 129.6 | 13.5 | 116.1 | 0.97605 | 5.692% | 1.2343 | 1.1057 | 53.11% | 90.87% | 321.0702 | 2.0818 | 43.2786 | 2081.763 | 51.4838 | 72 | 75 | Steel | 140 | 455.6284 | 4.4697 | 136.6885 | 1.3409 | 44.6971 | 4.464 | 0.19953 | 1.5404 | 1.24% | 4071.5006 | 122.145 | 0.5113 | 0.30315 | 0.31867 | 366.4351 | 522.195 | 0.49978 | 0.82463 | 0.82463 | 80 | 0% | 0.82463 | 0.82463 | 0.82463 | 0.4614% | 1.3944 | 216.8981 | 2.1278 | 65.0694 | 0.63833 | 21.2777 | 0.094984 | 0.73331 | 0.23973 | 0 | 0.057193 | 25 | 750
11F | Riser to 1st floor | Flow | 1 | 36 | 108 | 210 | 4 |  |  | 1 |  | 10 | 40 | 173.24 | 0.074034 | 173.24 | 4 | 14.4367 | 0.95 | 102.6 | 11.4 | 91.2 | 0.82495 | 5.051% | 0.97714 | 0.86857 | 51.29% | 91.25% | 264.44 | 1.6935 | 42.822 | 1693.5238 | 46.4356 | 51 | 54 | Copper | 140 | 1664.4323 | 16.3281 | 66.5773 | 0.65312 | 163.2808 | 1.02 | 0.16655 | 0.81967 | 0.6597% | 2042.8189 | 8.1713 | 0.82901 | 0.47833 | 0.50195 | 24.5138 | 155.76 | 0.38539 | 0.084786 | 0.84786 | 80 | 1% | 0.084786 | 0.84786 | 0.84786 | 0.4744% | 1.1785 | 850.4511 | 8.3429 | 34.018 | 0.33372 | 83.4293 | 0.085098 | 0.41881 | 0.40383 | 0 | 0.090757 | 17.4667 | 698.6667
12F | Riser to 2nd floor | Flow | 0.7 | 24 | 72 | 140 | 4 |  |  | 1 |  | 10 | 40 | 138.2608 | 0.088629 | 138.2608 | 4 | 11.5217 | 0.95 | 68.4 | 11.4 | 57 | 0.65838 | 4.219% | 0.65143 | 0.54286 | 45.19% | 90.72% | 195.2608 | 1.2012 | 41.2978 | 1716.06 | 46.7435 | 51 | 54 | Copper | 140 | 881.0901 | 8.6435 | 35.2436 | 0.34574 | 86.4349 | 1.02 | 0.088164 | 0.4339 | 0.3492% | 2042.8189 | 8.1713 | 0.58803 | 0.31889 | 0.33465 | 24.5138 | 131.2461 | 0.38539 | 0.084786 | 0.84786 | 80 | 2% | 0.084786 | 0.84786 | 0.84786 | 0.4744% | 0.94055 | 560.0769 | 5.4944 | 22.4031 | 0.21977 | 54.9435 | 0.056042 | 0.27582 | 0.32229 | 0 | 0.0662 | 17.4667 | 698.6667
13F | Riser to 3rd floor | Flow | 0.7 | 12 | 36 | 70 | 4 |  |  |  | 1 | 10 | 40 | 97.0051 | 0.12437 | 97.0051 | 3 | 8.0838 | 0.95 | 34.2 | 8.55 | 25.65 | 0.46193 | 3.007% | 0.32571 | 0.24429 | 34.59% | 89.79% | 122.6551 | 0.70621 | 38.6477 | 1008.8783 | 35.8405 | 39 | 42 | Copper | 140 | 1215.16 | 11.9207 | 48.6064 | 0.47683 | 119.2072 | 2.34 | 0.27894 | 0.75577 | 0.6083% | 1194.5896 | 4.7784 | 0.59118 | 0.27266 | 0.28743 | 14.3351 | 106.7323 | 0.3193 | 0.070246 | 0.70246 | 80 | 3% | 0.070246 | 0.70246 | 0.70246 | 0.3931% | 0.6599 | 1071.7029 | 10.5134 | 42.8681 | 0.42054 | 105.1341 | 0.24601 | 0.66655 | 0.38668 | 0 | 0.067051 | 13.3933 | 535.7333
14F | Lateral | Periphery | 0.7 | 6 | 18 | 35 | 10 |  |  | 1 |  | 80 | 800 | 70.7904 | 0.35 | 136.5 | 3 | 11.375 | 1 | 18 | 9 | 9 | 0.65 | 1.068% | 0.17143 | 0.085714 | 11.65% | 86.06% | 145.5 | 0.73571 | 32.9126 | 1051.0204 | 36.5814 | 39 | 42 | Copper | 140 | 1310.8346 | 12.8593 | 131.0835 | 1.2859 | 128.5929 | 0.78 | 0.1003 | 1.3862 | 1.116% | 1194.5896 | 11.9459 | 0.61587 | 0.1435 | 0.15629 | 35.8377 | 92.3972 | 0.3193 | 0.17561 | 14.0491 | 80 | 10% | 0.17561 | 14.0491 | 14.0491 | 7.861% | 0.92857 | 2017.4205 | 19.7909 | 201.7421 | 1.9791 | 197.909 | 0.15437 | 2.1335 | 0.54412 | 0 | 0.056241 | 13.3933 | 10714.6667
15F | Lateral | Periphery | 0.7 | 4 | 12 | 23.3333 | 6 |  |  | 1 |  | 80 | 480 | 59.96 | 0.5 | 130 | 2 | 10.8333 | 1 | 12 | 6 | 6 | 0.61905 | 0.7479% | 0.11429 | 0.057143 | 8.451% | 86.06% | 136 | 0.67619 | 32.1127 | 965.9864 | 35.0704 | 39 | 42 | Copper | 140 | 1121.2187 | 10.9992 | 67.2731 | 0.65995 | 109.9916 | 0.78 | 0.085793 | 0.74574 | 0.6002% | 1194.5896 | 7.1675 | 0.56604 | 0.095669 | 0.10715 | 21.5026 | 56.5596 | 0.3193 | 0.10537 | 8.4295 | 80 | 60% | 0.10537 | 8.4295 | 8.4295 | 4.717% | 0.88435 | 1843.121 | 18.081 | 110.5873 | 1.0849 | 180.8102 | 0.14103 | 1.2259 | 0.51821 | 0 | 0.044814 | 13.3933 | 6428.8
16F | Lateral | Periphery | 0.7 | 2 | 6 | 11.6667 | 6 |  |  |  | 1 | 80 | 480 | 46.5672 | 0.8 | 104 | 2 | 8.6667 | 1 | 6 | 6 | 0 | 0.49524 | 0.4674% | 0.057143 | 0 | 0% | 0% | 104 | 0.49524 | 30 | 707.483 | 30.0133 | 32.6 | 35 | Copper | 140 | 1506.4776 | 14.7785 | 90.3887 | 0.88671 | 147.7855 | 1.956 | 0.28907 | 1.1758 | 0.9463% | 834.689 | 5.0081 | 0.59332 | 0.06846 | 0.079437 | 15.0244 | 35.0569 | 0.2803 | 0.092498 | 7.3999 | 80 | 70% | 0.092498 | 7.3999 | 7.3999 | 4.141% | 0.70748 | 2916.3599 | 28.6095 | 174.9816 | 1.7166 | 286.0949 | 0.5596 | 2.2762 | 0.59332 | 0 | 0.040564 | 10.98 | 5270.4
18F | Feed | Periphery | 0.5 | 1 | 3 | 5.8333 | 8 | 5 |  |  |  | 480 | 3840 | 37.59 | 1 | 65 | 1 | 5.4167 | 1 | 3 | 3 | 0 | 0.30952 | 0.3739% | 0.028571 | 0 | 0% | 0% | 65 | 0.30952 | 30 | 619.0476 | 28.0748 | 32.6 | 35 | Copper | 140 | 630.8593 | 6.1887 | 50.4687 | 0.4951 | 61.8873 | 4.89 | 0.30263 | 0.79773 | 0.642% | 834.689 | 6.6775 | 0.37083 | 0.03423 | 0.041006 | 20.0325 | 20.0325 | 0.2803 | 0.12333 | 59.199 | 80 | 80% | 0.12333 | 59.199 | 59.199 | 33.13% | 0.44218 | 1221.2678 | 11.9806 | 97.7014 | 0.95845 | 119.8064 | 0.58585 | 1.5443 | 0.37083 | 0 | 0.022676 | 10.98 | 42163.2
HIU | Load | Load |  | 1 | 3 | 5.8333 | [5 empty] | 480 |  | 37.59 | 1 | 65 | 1 | 5.4167 | 1 | 3 | 3 | 0 | 0.30952 | 0.3739% | 0.028571 | 0 | 0% | 0% | 65 | 0.30952 | 30 | [13 empty] | 65 | 52.31% | [16 empty] | 0.44218 |  |  | 0 |  |  |  | 65
1F | Run to 1st riser | Return | 1 | 480 | 1440 | 2800 | 100 | 4 | 0 | 1 | 0 | 1 | 100 | 1000.6874 | 0.032073 | 1000.6874 | 23 | 83.3906 | 0.75 | 1080 | 51.75 | 1028.25 | 4.7652 | 11.66% | 10.2857 | 9.7929 | 67.27% | 89.81% | 2028.9374 | 14.558 | 46.8169 | 14558.0351 | 136.1465 | 147 | 150 | Steel | 140 | 518.4551 | 5.086 | 518.4551 | 5.086 | 50.8604 | 20.58 | 1.0467 | 6.1328 | 4.936% | 16971.6546 | 1697.1655 | 0.85779 | 0.60605 | 0.64052 |  |  | 0.90371 | 1.9716 | 1.9716 | 80 | 50% | 4.9704 | 4.9704 | 3.471 | 1.942% | 6.8074 | 126.8603 | 1.2445 | 126.8603 | 1.2445 | 12.445 | 0.25612 | 1.5006 | 0.28077 | 0 | 0.095869 | 50 | 5000
2F | Run to 2nd Riser | Return | 1 | 432 | 1296 | 2520 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 922.4307 | 0.03285 | 922.4307 | 21 | 76.8692 | 0.8 | 1036.8 | 50.4 | 986.4 | 4.3925 | 11.38% | 9.8743 | 9.3943 | 68.14% | 90.38% | 1908.8307 | 13.7868 | 47.0349 | 13786.8127 | 132.4912 | 147 | 150 | Steel | 140 | 468.7399 | 4.5983 | 140.622 | 1.3795 | 45.9834 | 7.644 | 0.3515 | 1.731 | 1.393% | 16971.6546 | 509.1496 | 0.81234 | 0.58181 | 0.61244 |  |  | 0.90371 | 0.59739 | 0.59739 | 80 | 0% | 1.4911 | 1.4911 | 0.59739 | 0.3343% | 6.275 | 109.1014 | 1.0703 | 32.7304 | 0.32109 | 10.7028 | 0.081813 | 0.4029 | 0.25882 | 0 | 0.087321 | 50 | 1500
3F | Run to 3rd Riser | Return | 1 | 384 | 1152 | 2240 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 842.9633 | 0.033773 | 842.9633 | 19 | 70.2469 | 0.8 | 921.6 | 45.6 | 876 | 4.0141 | 11.07% | 8.7771 | 8.3429 | 67.52% | 90.37% | 1718.9633 | 12.357 | 46.8789 | 12356.9679 | 125.4328 | 147 | 150 | Steel | 140 | 382.7064 | 3.7543 | 114.8119 | 1.1263 | 37.5435 | 7.644 | 0.28698 | 1.4133 | 1.137% | 16971.6546 | 509.1496 | 0.72809 | 0.51716 | 0.54456 |  |  | 0.90371 | 0.59316 | 0.59316 | 80 | 0% | 1.4911 | 1.4911 | 0.59316 | 0.3319% | 5.7344 | 92.3359 | 0.90582 | 27.7008 | 0.27174 | 9.0582 | 0.069241 | 0.34099 | 0.23652 | 0 | 0.078701 | 50 | 1500
4F | Run to 4th Riser | Return | 1 | 336 | 1008 | 1960 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 762.0497 | 0.034892 | 762.0497 | 17 | 63.5041 | 0.8 | 806.4 | 40.8 | 765.6 | 3.6288 | 10.72% | 7.68 | 7.2914 | 66.77% | 90.36% | 1527.6497 | 10.9202 | 46.6925 | 10920.2366 | 117.9156 | 147 | 150 | Steel | 140 | 304.4042 | 2.9862 | 91.3212 | 0.89586 | 29.862 | 7.644 | 0.22827 | 1.1241 | 0.9047% | 16971.6546 | 509.1496 | 0.64344 | 0.45252 | 0.47665 |  |  | 0.90371 | 0.58811 | 0.58811 | 80 | 0% | 1.4911 | 1.4911 | 0.58811 | 0.3291% | 5.184 | 76.596 | 0.75141 | 22.9788 | 0.22542 | 7.5141 | 0.057438 | 0.28286 | 0.21382 | 0 | 0.069996 | 50 | 1500
5F | Run to 5th Riser | Return | 1 | 288 | 864 | 1680 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 679.3666 | 0.036291 | 679.3666 | 16 | 56.6139 | 0.85 | 734.4 | 40.8 | 693.6 | 3.2351 | 10.3% | 6.9943 | 6.6057 | 67.13% | 90.83% | 1372.9666 | 9.8408 | 46.7815 | 9840.7932 | 111.9361 | 147 | 150 | Steel | 140 | 251.0363 | 2.4627 | 75.3109 | 0.7388 | 24.6267 | 7.644 | 0.18825 | 0.92705 | 0.7461% | 16971.6546 | 509.1496 | 0.57984 | 0.41212 | 0.43241 |  |  | 0.90371 | 0.59052 | 0.59052 | 80 | 0% | 1.4911 | 1.4911 | 0.59052 | 0.3304% | 4.6215 | 61.9199 | 0.60743 | 18.576 | 0.18223 | 6.0743 | 0.046432 | 0.22866 | 0.19062 | 0 | 0.061187 | 50 | 1500
6F | Run to 6th Riser | Return | 1 | 240 | 720 | 1400 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 594.4483 | 0.038106 | 594.4483 | 14 | 49.5374 | 0.85 | 612 | 35.7 | 576.3 | 2.8307 | 9.813% | 5.8286 | 5.4886 | 65.97% | 90.81% | 1170.7483 | 8.3193 | 46.4935 | 8319.2778 | 102.9196 | 147 | 150 | Steel | 140 | 183.9261 | 1.8043 | 55.1778 | 0.54129 | 18.0432 | 7.644 | 0.13792 | 0.67922 | 0.5467% | 16971.6546 | 509.1496 | 0.49019 | 0.34343 | 0.36048 |  |  | 0.90371 | 0.58272 | 0.58272 | 80 | 0% | 1.4911 | 1.4911 | 0.58272 | 0.3261% | 4.0439 | 48.354 | 0.47435 | 14.5062 | 0.14231 | 4.7435 | 0.03626 | 0.17857 | 0.16679 | 0 | 0.052248 | 50 | 1500
7F | Run to 7th Riser | Return | 1 | 192 | 576 | 1120 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 506.5804 | 0.040591 | 506.5804 | 12 | 42.215 | 0.85 | 489.6 | 30.6 | 459 | 2.4123 | 9.212% | 4.6629 | 4.3714 | 64.44% | 90.77% | 965.5804 | 6.7837 | 46.11 | 6783.7164 | 92.9371 | 97 | 100 | Steel | 140 | 952.7251 | 9.3462 | 285.8175 | 2.8039 | 93.4623 | 5.044 | 0.47142 | 3.2753 | 2.636% | 7389.8051 | 221.6942 | 0.91798 | 0.63099 | 0.66264 |  |  | 0.6349 | 0.40208 | 0.40208 | 80 | 0% | 1.0476 | 1.0476 | 0.40208 | 0.225% | 3.4461 | 271.7857 | 2.6662 | 81.5357 | 0.79987 | 26.6622 | 0.13448 | 0.93435 | 0.32643 | 0 | 0.099078 | 33.3333 | 1000
8F | Run to 8th Riser | Return | 1 | 144 | 432 | 840 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 414.56 | 0.044291 | 414.56 | 10 | 34.5467 | 0.9 | 388.8 | 27 | 361.8 | 1.9741 | 8.443% | 3.7029 | 3.4457 | 63.58% | 91.18% | 776.36 | 5.4198 | 45.8941 | 5419.8095 | 83.0706 | 97 | 100 | Steel | 140 | 628.6774 | 6.1673 | 188.6032 | 1.8502 | 61.6733 | 5.044 | 0.31108 | 2.1613 | 1.739% | 7389.8051 | 221.6942 | 0.73342 | 0.50108 | 0.52468 |  |  | 0.6349 | 0.39797 | 0.39797 | 80 | 0% | 1.0476 | 1.0476 | 0.39797 | 0.2227% | 2.8201 | 187.495 | 1.8393 | 56.2485 | 0.5518 | 18.3933 | 0.092776 | 0.64457 | 0.26714 | 0 | 0.07762 | 33.3333 | 1000
9F | Run to 9th Riser | Return | 1 | 96 | 288 | 560 | 30 | 0 | 2 | 1 | 0 | 1 | 30 | 316.0416 | 0.050648 | 316.0416 | 8 | 26.3368 | 0.9 | 259.2 | 21.6 | 237.6 | 1.505 | 7.383% | 2.4686 | 2.2629 | 60.06% | 91.06% | 553.6416 | 3.7678 | 45.0144 | 3767.8173 | 69.2628 | 72 | 75 | Steel | 140 | 1367.0816 | 13.4111 | 410.1245 | 4.0233 | 134.1107 | 3.744 | 0.50211 | 4.5254 | 3.642% | 4071.5006 | 122.145 | 0.92541 | 0.60631 | 0.63537 |  |  | 0.49978 | 0.30008 | 0.30008 | 80 | 0% | 0.82463 | 0.82463 | 0.30008 | 0.1679% | 2.1499 | 483.6495 | 4.7446 | 145.0949 | 1.4234 | 47.446 | 0.17764 | 1.601 | 0.36963 | 0 | 0.10044 | 25 | 750
10F | Run to 10th riser (ground floor) | Return | 1 | 48 | 144 | 280 | 30 | 1 | 2 | 0 | 0 | 1 | 30 | 204.9702 | 0.065696 | 204.9702 | 5 | 17.0809 | 0.9 | 129.6 | 13.5 | 116.1 | 0.97605 | 5.692% | 1.2343 | 1.1057 | 53.11% | 90.87% | 321.0702 | 2.0818 | 43.2786 | 2081.763 | 51.4838 | 72 | 75 | Steel | 140 | 455.6284 | 4.4697 | 136.6885 | 1.3409 | 44.6971 | 4.464 | 0.19953 | 1.5404 | 1.24% | 4071.5006 | 122.145 | 0.5113 | 0.30315 | 0.31867 |  |  | 0.49978 | 0.27406 | 0.27406 | 80 | 0% | 0.82463 | 0.82463 | 0.27406 | 0.1534% | 1.3944 | 216.8981 | 2.1278 | 65.0694 | 0.63833 | 21.2777 | 0.094984 | 0.73331 | 0.23973 | 0 | 0.057193 | 25 | 750
11F | Riser to 1st floor | Return | 1 | 36 | 108 | 210 | 4 | 0 | 0 | 1 | 0 | 10 | 40 | 173.24 | 0.074034 | 173.24 | 4 | 14.4367 | 0.95 | 102.6 | 11.4 | 91.2 | 0.82495 | 5.051% | 0.97714 | 0.86857 | 51.29% | 91.25% | 264.44 | 1.6935 | 42.822 | 1693.5238 | 46.4356 | 51 | 54 | Copper | 140 | 1664.4323 | 16.3281 | 66.5773 | 0.65312 | 163.2808 | 1.02 | 0.16655 | 0.81967 | 0.6597% | 2042.8189 | 8.1713 | 0.82901 | 0.47833 | 0.50195 |  |  | 0.38539 | 0.027474 | 0.27474 | 80 | 1% | 0.084786 | 0.84786 | 0.28047 | 0.1569% | 1.1785 | 850.4511 | 8.3429 | 34.018 | 0.33372 | 83.4293 | 0.085098 | 0.41881 | 0.40383 | 0 | 0.090757 | 17.4667 | 698.6667
12F | Riser to 2nd floor | Return | 0.7 | 24 | 72 | 140 | 4 | 0 | 0 | 1 | 0 | 10 | 40 | 138.2608 | 0.088629 | 138.2608 | 4 | 11.5217 | 0.95 | 68.4 | 11.4 | 57 | 0.65838 | 4.219% | 0.65143 | 0.54286 | 45.19% | 90.72% | 195.2608 | 1.2012 | 41.2978 | 1716.06 | 46.7435 | 51 | 54 | Copper | 140 | 881.0901 | 8.6435 | 35.2436 | 0.34574 | 86.4349 | 1.02 | 0.088164 | 0.4339 | 0.3492% | 2042.8189 | 8.1713 | 0.58803 | 0.31889 | 0.33465 |  |  | 0.38539 | 0.025124 | 0.25124 | 80 | 2% | 0.084786 | 0.84786 | 0.26317 | 0.1473% | 0.94055 | 560.0769 | 5.4944 | 22.4031 | 0.21977 | 54.9435 | 0.056042 | 0.27582 | 0.32229 | 0 | 0.0662 | 17.4667 | 698.6667
13F | Riser to 3rd floor | Return | 0.7 | 12 | 36 | 70 | 4 | 0 | 0 | 0 | 1 | 10 | 40 | 97.0051 | 0.12437 | 97.0051 | 3 | 8.0838 | 0.95 | 34.2 | 8.55 | 25.65 | 0.46193 | 3.007% | 0.32571 | 0.24429 | 34.59% | 89.79% | 122.6551 | 0.70621 | 38.6477 | 1008.8783 | 35.8405 | 39 | 42 | Copper | 140 | 1215.16 | 11.9207 | 48.6064 | 0.47683 | 119.2072 | 2.34 | 0.27894 | 0.75577 | 0.6083% | 1194.5896 | 4.7784 | 0.59118 | 0.27266 | 0.28743 |  |  | 0.3193 | 0.017431 | 0.17431 | 80 | 3% | 0.070246 | 0.70246 | 0.19015 | 0.1064% | 0.6599 | 1071.7029 | 10.5134 | 42.8681 | 0.42054 | 105.1341 | 0.24601 | 0.66655 | 0.38668 | 0 | 0.067051 | 13.3933 | 535.7333
14F | Lateral | Return | 0.7 | 6 | 18 | 35 | 10 | 0 | 0 | 1 | 0 | 80 | 800 | 70.7904 | 0.35 | 136.5 | 3 | 11.375 | 1 | 18 | 9 | 9 | 0.65 | 1.068% | 0.17143 | 0.085714 | 11.65% | 86.06% | 145.5 | 0.73571 | 32.9126 | 1051.0204 | 36.5814 | 39 | 42 | Copper | 140 | 1310.8346 | 12.8593 | 131.0835 | 1.2859 | 128.5929 | 0.78 | 0.1003 | 1.3862 | 1.116% | 1194.5896 | 11.9459 | 0.61587 | 0.1435 | 0.15629 |  |  | 0.3193 | 0.025265 | 2.0212 | 80 | 10% | 0.17561 | 14.0491 | 3.224 | 1.804% | 0.92857 | 2017.4205 | 19.7909 | 201.7421 | 1.9791 | 197.909 | 0.15437 | 2.1335 | 0.54412 | 0 | 0.056241 | 13.3933 | 10714.6667
15F | Lateral | Return | 0.7 | 4 | 12 | 23.3333 | 6 | 0 | 0 | 1 | 0 | 80 | 480 | 59.96 | 0.5 | 130 | 2 | 10.8333 | 1 | 12 | 6 | 6 | 0.61905 | 0.7479% | 0.11429 | 0.057143 | 8.451% | 86.06% | 136 | 0.67619 | 32.1127 | 965.9864 | 35.0704 | 39 | 42 | Copper | 140 | 1121.2187 | 10.9992 | 67.2731 | 0.65995 | 109.9916 | 0.78 | 0.085793 | 0.74574 | 0.6002% | 1194.5896 | 7.1675 | 0.56604 | 0.095669 | 0.10715 |  |  | 0.3193 | 0.013626 | 1.0901 | 80 | 60% | 0.10537 | 8.4295 | 5.4937 | 3.074% | 0.88435 | 1843.121 | 18.081 | 110.5873 | 1.0849 | 180.8102 | 0.14103 | 1.2259 | 0.51821 | 0 | 0.044814 | 13.3933 | 6428.8
16F | Lateral | Return | 0.7 | 2 | 6 | 11.6667 | 6 | 0 | 0 | 0 | 1 | 80 | 480 | 46.5672 | 0.8 | 104 | 2 | 8.6667 | 1 | 6 | 6 | 0 | 0.49524 | 0.4674% | 0.057143 | 0 | 0% | 0% | 104 | 0.49524 | 30 | 707.483 | 30.0133 | 32.6 | 35 | Copper | 140 | 1506.4776 | 14.7785 | 90.3887 | 0.88671 | 147.7855 | 1.956 | 0.28907 | 1.1758 | 0.9463% | 834.689 | 5.0081 | 0.59332 | 0.06846 | 0.079437 |  |  | 0.2803 | 0.0084089 | 0.67272 | 80 | 70% | 0.092498 | 7.3999 | 5.3817 | 3.011% | 0.70748 | 2916.3599 | 28.6095 | 174.9816 | 1.7166 | 286.0949 | 0.5596 | 2.2762 | 0.59332 | 0 | 0.040564 | 10.98 | 5270.4
18F | Feed | Return | 0.5 | 1 | 3 | 5.8333 | 8 | 5 | 0 | 0 | 0 | 480 | 3840 | 37.59 | 1 | 65 | 1 | 5.4167 | 1 | 3 | 3 | 0 | 0.30952 | 0.3739% | 0.028571 | 0 | 0% | 0% | 65 | 0.30952 | 30 | 619.0476 | 28.0748 | 32.6 | 35 | Copper | 140 | 630.8593 | 6.1887 | 50.4687 | 0.4951 | 61.8873 | 4.89 | 0.30263 | 0.79773 | 0.642% | 834.689 | 6.6775 | 0.37083 | 0.03423 | 0.041006 |  |  | 0.2803 | 0.011212 | 5.3817 | 80 | 80% | 0.12333 | 59.199 | 48.4355 | 27.1% | 0.44218 | 1221.2678 | 11.9806 | 97.7014 | 0.95845 | 119.8064 | 0.58585 | 1.5443 | 0.37083 | 0 | 0.022676 | 10.98 | 42163.2
[13 empty] | 12180 | [27 empty] | 49.179 |  |  | 10.0704 | 124.2494 |  |  | 4982.512 | 0.37083 |  | 0.66264 |  |  |  |  | 123.8097 |  |  |  |  | 178.7118 | [8 empty] | 95.7777 |  |  |  |  | 165020.2667
| Dwelling Peak DHW | 65 |  | Kw | [43 empty] | 9965.024
| Dwelling Peak CH | 3 |  | Kw | [40 empty] | Building | [15 empty] | 23.9675 | [8 empty] | Building |  |  |  |  | per property
| DP across load (HIU+meter) | 65 |  | kPa | [40 empty] | 77.2297 | [15 empty] | on network | [8 empty] | 82.082 |  |  |  |  | 343.7922
| Peak Load Flow Temperature | 80 |  | C | [40 empty] | kPa | [24 empty] | kPa
| Summer Flow Temperature | 65 |  | C | [56 empty] | 154.7443
| Return DHW | 30 |  | C | [56 empty] | in buildings
| Return CH | 55 |  | C
| Occupants per property | 3
| Flush Rate (HIU function) | 20 |  | l/m
| Peak continuous velocity | 1 |  | m/s
| Fixed DHW/property/day | 50 |  | litres
| DHW/person/day | 25 |  | litres
| DHW Temp Rise (for above) | 40
| Average tap load | 12 |  | kW
| DHW Priority (0/1) | 1
http://www.katmarsoftware.com/articles/pipe-fitting-pressure-drop.htm
| Descroption | L/D
| Ball valve, full bore | 3
| Ball valve, reduced bore | 25
| Tee, Inline | 20
| Tee, Branch | 60
| 90° screwed elbow | 30
| 90° long radius bend | 13
| 45° screwed elbow | 16
| 45° long radius bend | 10
Note on E7: Used to select appropriate pipe size.
Note on Q7: For calculation of DHW diversity.
Note on R7: The DHW load used in calculation.
Note on T7: Not used in any calculaton
Note on AQ7: In a real calculation, pressure calculated pressure drops should be checked against pipe manufacturers pressure drop data.
Note on BC7: Green if under 30s. Yellow if under 60s. With HIU keep warm timed, longer delays are allowable. 1 minute initially selected as maximum allowed time waiting outside keep warm times.
Note on BQ7: In a real calculation, pressure calculated pressure drops should be checked against pipe manufacturers pressure drop data.
Note on R24: 10 or above properties and diversity follows a recognised standard.
Note on E25: Lateral set to 1.5 for noise reasons.
Note on E43: Lateral set to 1.5 for noise reasons.

## Plantroom Sizing
Hour | EST Volume | % | DHW kWh | Max time at peak diversity | Start | End of DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW | Net kWh | kWh at Start | kWh end DHW
1 | 2.25 | 1.828% | 51.1779 | 5.114% | 0:00 | 0:03 | 70.5721 | 0 | -44.9513 | 195.5721 | 0 | -38.5584 | 320.5721 | 0 | -32.1656 | 420.5721 | 0 | -27.0513 | 570.5721 | 0 | -19.3799 | 670.5721 | 0 | -14.2656
2 | 1.5 | 1.219% | 34.1186 | 3.41% | 1:00 | 1:02 | 87.6314 | 0 | -29.9675 | 212.6314 | 0 | -25.7056 | 337.6314 | 0 | -21.4437 | 437.6314 | 0 | -18.0342 | 587.6314 | 0 | -12.9199 | 687.6314 | 0 | -9.5104
3 | 1.25 | 1.015% | 28.4322 | 2.841% | 2:00 | 2:02 | 93.3178 | 0 | -24.9729 | 218.3178 | 0 | -21.4214 | 343.3178 | 0 | -17.8698 | 443.3178 | 0 | -15.0285 | 593.3178 | 0 | -10.7666 | 693.3178 | 0 | -7.9253
4 | 1 | 0.8123% | 22.7457 | 2.273% | 3:00 | 3:01 | 99.0043 | 0 | -19.9783 | 224.0043 | 0 | -17.1371 | 349.0043 | 0 | -14.2958 | 449.0043 | 0 | -12.0228 | 599.0043 | 0 | -8.6133 | 699.0043 | 0 | -6.3403
5 | 1.6 | 1.3% | 36.3932 | 3.637% | 4:00 | 4:02 | 85.3568 | 0 | -31.9654 | 210.3568 | 0 | -27.4193 | 335.3568 | 0 | -22.8733 | 435.3568 | 0 | -19.2365 | 585.3568 | 0 | -13.7813 | 685.3568 | 0 | -10.1444
6 | 2.1 | 1.706% | 47.766 | 4.773% | 5:00 | 5:03 | 73.984 | 0 | -41.9545 | 198.984 | 0 | -35.9879 | 323.984 | 0 | -30.0212 | 423.984 | 0 | -25.2479 | 573.984 | 0 | -18.0879 | 673.984 | 0 | -13.3146
7 | 5.5 | 4.468% | 125.1015 | 12.5% | 6:00 | 6:08 | -3.3515 | 0 | -109.8809 | 121.6485 | 0 | -94.2539 | 246.6485 | 0 | -78.627 | 346.6485 | 0 | -66.1254 | 496.6485 | 0 | -47.3731 | 596.6485 | 0 | -34.8715
8 | 10.7 | 8.692% | 243.3794 | 24.32% | 7:00 | 7:15 | -121.6294 | -3.3515 | -217.1198 | 3.3706 | 0 | -183.3668 | 128.3706 | 0 | -152.9652 | 228.3706 | 0 | -128.644 | 378.3706 | 0 | -92.1622 | 478.3706 | 0 | -67.841
9 | 9.3 | 7.555% | 211.5353 | 21.14% | 8:00 | 8:13 | -89.7853 | -124.9809 | -310.7795 | 35.2147 | 0 | -159.3748 | 160.2147 | 0 | -132.9511 | 260.2147 | 0 | -111.8121 | 410.2147 | 0 | -80.1036 | 510.2147 | 0 | -58.9646
10 | 7.5 | 6.093% | 170.593 | 17.05% | 9:00 | 9:10 | -48.843 | -214.7662 | -364.6038 | 76.157 | 0 | -128.5281 | 201.157 | 0 | -107.2186 | 301.157 | 0 | -90.171 | 451.157 | 0 | -64.5997 | 551.157 | 0 | -47.5521
11 | 6.7 | 5.443% | 152.3964 | 15.23% | 10:00 | 10:09 | -30.6464 | -263.6093 | -397.4642 | 94.3536 | 0 | -114.8184 | 219.3536 | 0 | -95.782 | 319.3536 | 0 | -80.5528 | 469.3536 | 0 | -57.709 | 569.3536 | 0 | -42.4799
12 | 5.9 | 4.793% | 134.1998 | 13.41% | 11:00 | 11:08 | -12.4498 | -294.2557 | -412.1279 | 112.5502 | 0 | -101.1088 | 237.5502 | 0 | -84.3453 | 337.5502 | 0 | -70.9346 | 487.5502 | 0 | -50.8184 | 587.5502 | 0 | -37.4076
13 | 5.2 | 4.224% | 118.2778 | 11.82% | 12:00 | 12:07 | 3.4722 | -306.7055 | -410.5929 | 128.4722 | 0 | -89.1128 | 253.4722 | 0 | -74.3382 | 353.4722 | 0 | -62.5186 | 503.4722 | 0 | -44.7891 | 603.4722 | 0 | -32.9694
14 | 4.4 | 3.574% | 100.0812 | 10% | 13:00 | 13:06 | 21.6688 | -303.2333 | -391.1381 | 146.6688 | 0 | -75.4032 | 271.6688 | 0 | -62.9016 | 371.6688 | 0 | -52.9003 | 521.6688 | 0 | -37.8985 | 621.6688 | 0 | -27.8972
15 | 3.8 | 3.087% | 86.4338 | 8.637% | 14:00 | 14:05 | 35.3162 | -281.5646 | -357.4823 | 160.3162 | 0 | -65.1209 | 285.3162 | 0 | -54.3241 | 385.3162 | 0 | -45.6867 | 535.3162 | 0 | -32.7305 | 635.3162 | 0 | -24.0931
16 | 3.9 | 3.168% | 88.7084 | 8.865% | 15:00 | 15:05 | 33.0416 | -246.2484 | -324.1639 | 158.0416 | 0 | -66.8346 | 283.0416 | 0 | -55.7537 | 383.0416 | 0 | -46.8889 | 533.0416 | 0 | -33.5918 | 633.0416 | 0 | -24.7271
17 | 4.5 | 3.656% | 102.3558 | 10.23% | 16:00 | 16:06 | 19.3942 | -213.2067 | -303.1093 | 144.3942 | 0 | -77.1169 | 269.3942 | 0 | -64.3312 | 369.3942 | 0 | -54.1026 | 519.3942 | 0 | -38.7598 | 619.3942 | 0 | -28.5312
18 | 6.5 | 5.28% | 147.8473 | 14.77% | 17:00 | 17:09 | -26.0973 | -193.8126 | -323.6718 | 98.9027 | 0 | -111.391 | 223.9027 | 0 | -92.9228 | 323.9027 | 0 | -78.1482 | 473.9027 | 0 | -55.9864 | 573.9027 | 0 | -41.2118
19 | 9.5 | 7.717% | 216.0845 | 21.59% | 18:00 | 18:13 | -94.3345 | -219.9098 | -409.7041 | 30.6655 | 0 | -162.8023 | 155.6655 | 0 | -135.8103 | 255.6655 | 0 | -114.2166 | 405.6655 | 0 | -81.8262 | 505.6655 | 0 | -60.2326
20 | 9 | 7.311% | 204.7116 | 20.46% | 19:00 | 19:12 | -82.9616 | -314.2443 | -494.0494 | 42.0384 | 0 | -154.2337 | 167.0384 | 0 | -128.6623 | 267.0384 | 0 | -108.2052 | 417.0384 | 0 | -77.5196 | 517.0384 | 0 | -57.0625
21 | 7.5 | 6.093% | 170.593 | 17.05% | 20:00 | 20:10 | -48.843 | -397.2059 | -547.0435 | 76.157 | 0 | -128.5281 | 201.157 | 0 | -107.2186 | 301.157 | 0 | -90.171 | 451.157 | 0 | -64.5997 | 551.157 | 0 | -47.5521
22 | 6 | 4.874% | 136.4744 | 13.64% | 21:00 | 21:08 | -14.7244 | -446.0489 | -565.919 | 110.2756 | 0 | -102.8225 | 235.2756 | 0 | -85.7749 | 335.2756 | 0 | -72.1368 | 485.2756 | 0 | -51.6797 | 585.2756 | 0 | -38.0417
23 | 4.5 | 3.656% | 102.3558 | 10.23% | 22:00 | 22:06 | 19.3942 | -460.7734 | -550.6759 | 144.3942 | 0 | -77.1169 | 269.3942 | 0 | -64.3312 | 369.3942 | 0 | -54.1026 | 519.3942 | 0 | -38.7598 | 619.3942 | 0 | -28.5312
24 | 3 | 2.437% | 68.2372 | 6.819% | 23:00 | 23:04 | 53.5128 | -441.3792 | -501.3142 | 178.5128 | 0 | -51.4112 | 303.5128 | 0 | -42.8874 | 403.5128 | 0 | -36.0684 | 553.5128 | 0 | -25.8399 | 653.5128 | 0 | -19.0208
1 | [7 empty] | -387.8664 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | [7 empty] | -317.2943 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [7 empty] | -229.6629 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [7 empty] | -136.345 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [7 empty] | -37.3408 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
6 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7 | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
8 | [7 empty] | -3.3515 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Total | 123.1 | 100% | 2800 | [5 empty] | 1 |  |  | 1.1 |  |  | 1.2 |  |  | 1.3 |  |  | 1.4 |  |  | 1.5
DHW kW |  |  | 116.6667 | [5 empty] | 1150 | kW |  | 1275 |  |  | 1400 |  |  | 1500 |  |  | 1650 |  |  | 1750
Heating kW |  |  | 1028.25 | [5 empty] | 121.75 | kW |  | 246.75 |  |  | 371.75 |  |  | 471.75 |  |  | 621.75 |  |  | 721.75
Minimum Boiler Power |  |  | 1144.9167
[9 empty] | -565.919 | kWh |  | -183.3668 |  |  | -152.9652 |  |  | -128.644 |  |  | -92.1622 |  |  | -67.841
Selected Boiler Power | [8 empty] | 19402.9374 | litres |  | 6286.8603 |  |  | 5244.5223 |  |  | 4410.6519 |  |  | 3159.8464 |  |  | 2325.976
Spare for DHW
Min kWh
Central Buffer Volume
| Boiler Size | Buffer Size
| 1150 | 19402.9374
| 1275 | 6286.8603
| 1400 | 5244.5223
| 1500 | 4410.6519
| 1650 | 3159.8464
| 1750 | 2325.976
Note on E2: Calculted hourly volumes from EST Data weightings
Note on F2: With a known volume per hour, and a peak diversified flow, the maximum possible draw off is the hourly volume drawn in a single hit at full diversity.

## Pipes
Diameter | Wal | Bore | Material | Roughness Constant | Tube Thermal Conductivity | Insulation Thermal Conductivity | Insulation Thickness | Cost | ro | ri | rs | Thermal Loss
mm | mm | mm |  |  | W/mk | W/mK | mm | £/m |  |  |  | W/m/K
10 | 0.8 | 8.4 | Copper | 140 | 401 | 0.034 | 10 | 1.6784 | 0.005 | 0.0042 | 0.015 | 0.19445
12 | 0.8 | 10.4 | Copper | 140 | 401 | 0.034 | 10 | 2 | 0.006 | 0.0052 | 0.016 | 0.2178
15 | 1 | 13 | Copper | 140 | 401 | 0.034 | 10 | 2.0933 | 0.0075 | 0.0065 | 0.0175 | 0.25213
22 | 1 | 20 | Copper | 140 | 401 | 0.034 | 10 | 4.4867 | 0.011 | 0.01 | 0.021 | 0.33037
28 | 1 | 26 | Copper | 140 | 401 | 0.034 | 10 | 5.7133 | 0.014 | 0.013 | 0.024 | 0.39634
35 | 1.2 | 32.6 | Copper | 140 | 401 | 0.034 | 20 | 10.98 | 0.0175 | 0.0163 | 0.0375 | 0.2803
42 | 1.5 | 39 | Copper | 140 | 401 | 0.034 | 20 | 13.3933 | 0.021 | 0.0195 | 0.041 | 0.3193
54 | 1.5 | 51 | Copper | 140 | 401 | 0.034 | 20 | 17.4667 | 0.027 | 0.0255 | 0.047 | 0.38539
75 | 1.5 | 72 | Steel | 140 | 401 | 0.034 | 20 | 25 | 0.0375 | 0.036 | 0.0575 | 0.49978
100 | 1.5 | 97 | Steel | 140 | 401 | 0.034 | 20 | 33.3333 | 0.05 | 0.0485 | 0.07 | 0.6349
150 | 1.5 | 147 | Steel | 140 | 401 | 0.034 | 20 | 50 | 0.075 | 0.0735 | 0.095 | 0.90371
200 | 1.5 | 197 | Steel | 140 | 401 | 0.034 | 20 | 66.6667 | 0.1 | 0.0985 | 0.12 | 1.1717
250 | 1.5 | 247 | Steel | 140 | 401 | 0.034 | 20 | 83.3333 | 0.125 | 0.1235 | 0.145 | 1.4393
http://www.engineeringtoolbox.com/conductive-heat-loss-cylinder-pipe-d_1487.html
Q = (ti - to) / [(ln(ro / ri) / 2 π k L) + (ln(rs / ro) / 2 π ks L)]
http://www.insulationgiant.co.uk/Rockwool-Heating-and-Ventilation-Pipe-Insulation-40mm-Wall-Thickness/p/9000094465
Note on J2: Based on quoted prices for 100m lengths

## Energy Use
| Power |  | Hours/Year | Annual Energy
Losses in Buildings | 154.7443 | kW | 8760 | 1355560.1973 | kWh
Losses in Netork | 23.9675 | kW | 8760 | 209955.5678 | kWh
Domestic Hot Water |  |  |  | 1022000 | kWh
Central Heating | 1080 | kW | 500 | 540000 | kWh

## Energy Generation
NOT IMPLEMENTED YET
Chart of Boiler Efficiency at different Flow Temperatures
Temperature | Peak | 30 | 40 | 50 | 60 | 70 | 80 | 90
Gas Boiler | 90 | 95% | 95% | 95% | 95% | 90% | 85% | 80%
CHP | 90 | 100% | 100% | 100% | 100% | 100% | 90% | 80%
Heat Pump | 55 | 500% | 400% | 300% | 200% | 0% | 0% | 0%
Solar Thermal | 90 | 100% | 100% | 95% | 95% | 90% | 85% | 80%
Biomass | 90 | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Peak Load Flow Temperature | 85 | C |  | 85%
Summer Flow Temperature | 65 | C
Return DHW | 30 | C
Return CH | 55 | C